## Overview
CONSTANTS
One gallon of water weighs: | 8.34 | lbs
One gallon of water comprises: | 0.13368 | cu-ft
Hours in a week: | 168 | hours
Hours for cooldown in a week: | 166 | hours
BTU per ton of refrigeration: | 12000 | BTU
one refrigeration ton: | 3.5169 | Kw
Minutes per hour: | 60 | min
INPUT VALUES AND BASIC CALCS
Ambient (outside) Temperature [Tenv]: | 90 | deg F
Stillage temperature out of still: | 190 | deg F
Note on B2: Bob Glicksman: http://mathforum.org/library/drmath/view/56355.html
Note on B3: Bob Glicksman: http://wiki.answers.com/Q/How_many_cubic_feet_are_in_a_gallon
Note on B4: Bob Glicksman: 24 x 7 = 168
Note on B5: Bob Glicksman: 168 - 2 hours for transfer
Note on B6: Bob Glicksman: http://en.wikipedia.org/wiki/Ton_of_refrigeration
Note on B7: Bob Glicksman: http://www.rapidtables.com/convert/power/ton-to-kw.htm

## Fermentation Tank
CONSTANTS |  |  | FERMENTATION TANK HEAT LOSS vs TIME
One gallon of water weighs: | 8.34 | lbs
One gallon of water comprises: | 0.13368 | cu-ft | Time (hr) | Temp (deg F) | BTU/hr loss
|  |  | 0 | 90 | ---------
INPUT VALUES AND BASIC CALCS |  |  | 1 | 90 | 0
R-value: | 6 | (sq-ft * deltaT*hr)/BTU | 2 | 90 | 0
height of cylindrical tank: | 7 | ft | 3 | 90 | 0
diameter of cylindrical tank: | 12 | ft | 4 | 90 | 0
Initial temperature [T(0)]: | 90 | deg F | 5 | 90 | 0
Outside temperature [Tenv]: | 90 | deg F | 6 | 90 | 0
Volume of liquid in tank: | 4000 | gallons | 7 | 90 | 0
Volume of cylindrical tank = | 791.6813 | cu-ft | 8 | 90 | 0
Volume of cylindrical tank = | 5922.2124 | gallons | 9 | 90 | 0
Surface area of tank (top/bottom) = | 113.0973 | sq-ft | 10 | 90 | 0
Surface area of tank (side) = | 263.8938 | sq-ft | 11 | 90 | 0
Total surface area of tank = | 490.0885 | sq-ft | 12 | 90 | 0
A*h = A/R = | 81.6814 | BTU/(deltaT * hr) | 13 | 90 | 0
"k" = | 0.0024485 | deg F/(deltaT * hr) | 14 | 90 | 0
Mass of wort/beer= | 33360 | lb | 15 | 90 | 0
|  |  | 16 | 90 | 0
|  |  | 17 | 90 | 0
|  |  | 18 | 90 | 0
|  |  | 19 | 90 | 0
|  |  | 20 | 90 | 0
|  |  | 21 | 90 | 0
|  |  | 22 | 90 | 0
|  |  | 23 | 90 | 0
|  |  | 24 | 90 | 0
|  |  | 25 | 90 | 0
|  |  | 26 | 90 | 0
|  |  | 27 | 90 | 0
|  |  | 28 | 90 | 0
|  |  | 29 | 90 | 0
|  |  | 30 | 90 | 0
|  |  | 31 | 90 | 0
|  |  | 32 | 90 | 0
|  |  | 33 | 90 | 0
|  |  | 34 | 90 | 0
|  |  | 35 | 90 | 0
|  |  | 36 | 90 | 0
|  |  | 37 | 90 | 0
|  |  | 38 | 90 | 0
|  |  | 39 | 90 | 0
|  |  | 40 | 90 | 0
|  |  | 41 | 90 | 0
|  |  | 42 | 90 | 0
|  |  | 43 | 90 | 0
|  |  | 44 | 90 | 0
|  |  | 45 | 90 | 0
|  |  | 46 | 90 | 0
|  |  | 47 | 90 | 0
|  |  | 48 | 90 | 0
|  |  | 49 | 90 | 0
|  |  | 50 | 90 | 0
|  |  | 51 | 90 | 0
|  |  | 52 | 90 | 0
|  |  | 53 | 90 | 0
|  |  | 54 | 90 | 0
|  |  | 55 | 90 | 0
|  |  | 56 | 90 | 0
|  |  | 57 | 90 | 0
|  |  | 58 | 90 | 0
|  |  | 59 | 90 | 0
|  |  | 60 | 90 | 0
|  |  | 61 | 90 | 0
|  |  | 62 | 90 | 0
|  |  | 63 | 90 | 0
|  |  | 64 | 90 | 0
|  |  | 65 | 90 | 0
|  |  | 66 | 90 | 0
|  |  | 67 | 90 | 0
|  |  | 68 | 90 | 0
|  |  | 69 | 90 | 0
|  |  | 70 | 90 | 0
|  |  | 71 | 90 | 0
|  |  | 72 | 90 | 0
|  |  | 73 | 90 | 0
|  |  | 74 | 90 | 0
|  |  | 75 | 90 | 0
|  |  | 76 | 90 | 0
|  |  | 77 | 90 | 0
|  |  | 78 | 90 | 0
|  |  | 79 | 90 | 0
|  |  | 80 | 90 | 0
|  |  | 81 | 90 | 0
|  |  | 82 | 90 | 0
|  |  | 83 | 90 | 0
|  |  | 84 | 90 | 0
|  |  | 85 | 90 | 0
|  |  | 86 | 90 | 0
|  |  | 87 | 90 | 0
|  |  | 88 | 90 | 0
|  |  | 89 | 90 | 0
|  |  | 90 | 90 | 0
|  |  | 91 | 90 | 0
|  |  | 92 | 90 | 0
|  |  | 93 | 90 | 0
|  |  | 94 | 90 | 0
|  |  | 95 | 90 | 0
|  |  | 96 | 90 | 0
|  |  | 97 | 90 | 0
|  |  | 98 | 90 | 0
|  |  | 99 | 90 | 0
|  |  | 100 | 90 | 0
|  |  | 101 | 90 | 0
|  |  | 102 | 90 | 0
|  |  | 103 | 90 | 0
|  |  | 104 | 90 | 0
|  |  | 105 | 90 | 0
|  |  | 106 | 90 | 0
|  |  | 107 | 90 | 0
|  |  | 108 | 90 | 0
|  |  | 109 | 90 | 0
|  |  | 110 | 90 | 0
|  |  | 111 | 90 | 0
|  |  | 112 | 90 | 0
|  |  | 113 | 90 | 0
|  |  | 114 | 90 | 0
|  |  | 115 | 90 | 0
|  |  | 116 | 90 | 0
|  |  | 117 | 90 | 0
|  |  | 118 | 90 | 0
|  |  | 119 | 90 | 0
|  |  | 120 | 90 | 0
|  |  | 121 | 90 | 0
|  |  | 122 | 90 | 0
|  |  | 123 | 90 | 0
|  |  | 124 | 90 | 0
|  |  | 125 | 90 | 0
|  |  | 126 | 90 | 0
|  |  | 127 | 90 | 0
|  |  | 128 | 90 | 0
|  |  | 129 | 90 | 0
|  |  | 130 | 90 | 0
|  |  | 131 | 90 | 0
|  |  | 132 | 90 | 0
|  |  | 133 | 90 | 0
|  |  | 134 | 90 | 0
|  |  | 135 | 90 | 0
|  |  | 136 | 90 | 0
|  |  | 137 | 90 | 0
|  |  | 138 | 90 | 0
|  |  | 139 | 90 | 0
|  |  | 140 | 90 | 0
|  |  | 141 | 90 | 0
|  |  | 142 | 90 | 0
|  |  | 143 | 90 | 0
|  |  | 144 | 90 | 0
|  |  | 145 | 90 | 0
|  |  | 146 | 90 | 0
|  |  | 147 | 90 | 0
|  |  | 148 | 90 | 0
|  |  | 149 | 90 | 0
|  |  | 150 | 90 | 0
|  |  | 151 | 90 | 0
|  |  | 152 | 90 | 0
|  |  | 153 | 90 | 0
|  |  | 154 | 90 | 0
|  |  | 155 | 90 | 0
|  |  | 156 | 90 | 0
|  |  | 157 | 90 | 0
|  |  | 158 | 90 | 0
|  |  | 159 | 90 | 0
|  |  | 160 | 90 | 0
|  |  | 161 | 90 | 0
|  |  | 162 | 90 | 0
|  |  | 163 | 90 | 0
|  |  | 164 | 90 | 0
|  |  | 165 | 90 | 0
|  |  | 166 | 90 | 0
|  |  | 167 | 90 | 0
|  |  | 168 | 90 | 0
Note on G3: Bob Glicksman: Equation 6-4 and 6-5
Note on H3: Bob Glicksman: Equation 6-1

## Processing Tank
CONSTANTS |  |  | DYNAMIC TEMPERATURE VARIATION IN PROCESSING TANK
One gallon of water weighs: | 8.34 | lbs
One gallon of water comprises: | 0.13368 | cu-ft | Time (hr) | Old Volume (gal) | New Volume (gal) | "k" - based upon current (old) volume | Old Temp (deg F) | New Temp (deg F) | BTU/hr loss
Hours in a week: | 168 | hours
|  |  | 0 | 0 | 21.4286 | -------- | 0 | 190 | ------
INPUT VALUES AND BASIC CALCS |  |  | 1 | 21.4286 | 42.8571 | 0.68558 | 140.38 | 165.19 | 8867.798
R-value: | 4 | (sq-ft * deltaT*hr)/BTU | 2 | 42.8571 | 64.2857 | 0.34279 | 143.369 | 158.9127 | 3365.5417
height of cylindrical tank: | 7 | ft | 3 | 64.2857 | 85.7143 | 0.22853 | 144.8343 | 156.1257 | 1992.3025
diameter of cylindrical tank: | 12 | ft | 4 | 85.7143 | 107.1429 | 0.17139 | 145.7102 | 154.5682 | 1391.7573
Initial temperature [T(0)]: | 190 | deg F | 5 | 107.1429 | 128.5714 | 0.13712 | 146.295 | 153.5792 | 1060.4569
Outside temperature [Tenv]: | 90 | deg F | 6 | 128.5714 | 150 | 0.11426 | 146.7142 | 152.8979 | 852.3753
Ending volume of stillage in tank: | 3600 | gallons | 7 | 150 | 171.4286 | 0.097939 | 147.0297 | 152.401 | 710.3391
Volume of cylindrical tank = | 791.6813 | cu-ft | 8 | 171.4286 | 192.8571 | 0.085697 | 147.2762 | 152.0233 | 607.5902
Volume of cylindrical tank = | 5922.2124 | gallons | 9 | 192.8571 | 214.2857 | 0.076175 | 147.4741 | 151.7267 | 530.01
Surface area of tank (top/bottom) = | 113.0973 | sq-ft | 10 | 214.2857 | 235.7143 | 0.068558 | 147.6367 | 151.4879 | 469.4748
Surface area of tank (side) = | 263.8938 | sq-ft | 11 | 235.7143 | 257.1429 | 0.062325 | 147.7726 | 151.2916 | 420.9929
Total surface area of tank = | 490.0885 | sq-ft | 12 | 257.1429 | 278.5714 | 0.057131 | 147.8881 | 151.1274 | 381.3345
A*h = A/R = | 122.5221 | BTU/(deltaT * hr) | 13 | 278.5714 | 300 | 0.052737 | 147.9873 | 150.9882 | 348.3211
Static (final) value for "k" = | 0.0040808 | deg F/(deltaT * hr) | 14 | 300 | 321.4286 | 0.04897 | 148.0736 | 150.8687 | 320.4315
New gallons of stillage per hour = | 21.4286 | gal/hr | 15 | 321.4286 | 342.8571 | 0.045705 | 148.1493 | 150.765 | 296.5729
Mass of stillage = | 30024 | lbs | 16 | 342.8571 | 364.2857 | 0.042848 | 148.2163 | 150.6741 | 275.9404
Mass of feedstock = | 9360 | lbs | 17 | 364.2857 | 385.7143 | 0.040328 | 148.276 | 150.594 | 257.9284
Temperature of stillage = | 149.2092 | deg F | 18 | 385.7143 | 407.1429 | 0.038088 | 148.3295 | 150.5227 | 242.073
Temperature of feedstock = | 90 | deg F | 19 | 407.1429 | 428.5714 | 0.036083 | 148.3778 | 150.4589 | 228.0131
Temperature of the Mash = | 135.1375 | deg F | 20 | 428.5714 | 450 | 0.034279 | 148.4215 | 150.4015 | 215.4632
Heat needed for 115 deg F or above = | 0 | BTU | 21 | 450 | 471.4286 | 0.032646 | 148.4614 | 150.3495 | 204.1951
Stillage Temperature for 115 deg F Mash = | 122.7938 | deg F | 22 | 471.4286 | 492.8571 | 0.031163 | 148.4979 | 150.3023 | 194.0239
|  |  | 23 | 492.8571 | 514.2857 | 0.029808 | 148.5314 | 150.2592 | 184.7986
|  |  | 24 | 514.2857 | 535.7143 | 0.028566 | 148.5623 | 150.2198 | 176.3942
|  |  | 25 | 535.7143 | 557.1429 | 0.027423 | 148.5908 | 150.1835 | 168.7071
|  |  | 26 | 557.1429 | 578.5714 | 0.026368 | 148.6173 | 150.15 | 161.6499
|  |  | 27 | 578.5714 | 600 | 0.025392 | 148.6419 | 150.1189 | 155.1491
|  |  | 28 | 600 | 621.4286 | 0.024485 | 148.6648 | 150.0902 | 149.142
|  |  | 29 | 621.4286 | 642.8571 | 0.023641 | 148.6863 | 150.0634 | 143.5748
|  |  | 30 | 642.8571 | 664.2857 | 0.022853 | 148.7064 | 150.0384 | 138.4014
|  |  | 31 | 664.2857 | 685.7143 | 0.022115 | 148.7252 | 150.0151 | 133.5818
|  |  | 32 | 685.7143 | 707.1429 | 0.021424 | 148.743 | 149.9932 | 129.0812
|  |  | 33 | 707.1429 | 728.5714 | 0.020775 | 148.7597 | 149.9726 | 124.8693
|  |  | 34 | 728.5714 | 750 | 0.020164 | 148.7754 | 149.9533 | 120.9193
|  |  | 35 | 750 | 771.4286 | 0.019588 | 148.7904 | 149.9351 | 117.2077
|  |  | 36 | 771.4286 | 792.8571 | 0.019044 | 148.8045 | 149.9179 | 113.7138
|  |  | 37 | 792.8571 | 814.2857 | 0.018529 | 148.8179 | 149.9016 | 110.4192
|  |  | 38 | 814.2857 | 835.7143 | 0.018041 | 148.8306 | 149.8862 | 107.3073
|  |  | 39 | 835.7143 | 857.1429 | 0.017579 | 148.8427 | 149.8716 | 104.3635
|  |  | 40 | 857.1429 | 878.5714 | 0.017139 | 148.8542 | 149.8578 | 101.5747
|  |  | 41 | 878.5714 | 900 | 0.016721 | 148.8652 | 149.8446 | 98.929
|  |  | 42 | 900 | 921.4286 | 0.016323 | 148.8756 | 149.832 | 96.4158
|  |  | 43 | 921.4286 | 942.8571 | 0.015944 | 148.8857 | 149.8201 | 94.0253
|  |  | 44 | 942.8571 | 964.2857 | 0.015581 | 148.8952 | 149.8087 | 91.749
|  |  | 45 | 964.2857 | 985.7143 | 0.015235 | 148.9044 | 149.7978 | 89.5789
|  |  | 46 | 985.7143 | 1007.1429 | 0.014904 | 148.9132 | 149.7873 | 87.5077
|  |  | 47 | 1007.1429 | 1028.5714 | 0.014587 | 148.9216 | 149.7774 | 85.5289
|  |  | 48 | 1028.5714 | 1050 | 0.014283 | 148.9297 | 149.7678 | 83.6365
|  |  | 49 | 1050 | 1071.4286 | 0.013991 | 148.9374 | 149.7587 | 81.825
|  |  | 50 | 1071.4286 | 1092.8571 | 0.013712 | 148.9449 | 149.7499 | 80.0894
|  |  | 51 | 1092.8571 | 1114.2857 | 0.013443 | 148.9521 | 149.7414 | 78.425
|  |  | 52 | 1114.2857 | 1135.7143 | 0.013184 | 148.959 | 149.7333 | 76.8275
|  |  | 53 | 1135.7143 | 1157.1429 | 0.012935 | 148.9656 | 149.7255 | 75.2931
|  |  | 54 | 1157.1429 | 1178.5714 | 0.012696 | 148.9721 | 149.718 | 73.818
|  |  | 55 | 1178.5714 | 1200 | 0.012465 | 148.9783 | 149.7108 | 72.399
|  |  | 56 | 1200 | 1221.4286 | 0.012242 | 148.9842 | 149.7038 | 71.0328
|  |  | 57 | 1221.4286 | 1242.8571 | 0.012028 | 148.99 | 149.6971 | 69.7167
|  |  | 58 | 1242.8571 | 1264.2857 | 0.01182 | 148.9956 | 149.6906 | 68.448
|  |  | 59 | 1264.2857 | 1285.7143 | 0.01162 | 149.001 | 149.6843 | 67.2241
|  |  | 60 | 1285.7143 | 1307.1429 | 0.011426 | 149.0062 | 149.6783 | 66.0427
|  |  | 61 | 1307.1429 | 1328.5714 | 0.011239 | 149.0113 | 149.6724 | 64.9016
|  |  | 62 | 1328.5714 | 1350 | 0.011058 | 149.0162 | 149.6667 | 63.799
|  |  | 63 | 1350 | 1371.4286 | 0.010882 | 149.021 | 149.6613 | 62.7327
|  |  | 64 | 1371.4286 | 1392.8571 | 0.010712 | 149.0256 | 149.6559 | 61.7012
|  |  | 65 | 1392.8571 | 1414.2857 | 0.010547 | 149.03 | 149.6508 | 60.7026
|  |  | 66 | 1414.2857 | 1435.7143 | 0.010388 | 149.0344 | 149.6458 | 59.7356
|  |  | 67 | 1435.7143 | 1457.1429 | 0.010232 | 149.0386 | 149.641 | 58.7986
|  |  | 68 | 1457.1429 | 1478.5714 | 0.010082 | 149.0427 | 149.6363 | 57.8902
|  |  | 69 | 1478.5714 | 1500 | 0.0099359 | 149.0467 | 149.6317 | 57.0092
|  |  | 70 | 1500 | 1521.4286 | 0.0097939 | 149.0505 | 149.6273 | 56.1543
|  |  | 71 | 1521.4286 | 1542.8571 | 0.009656 | 149.0543 | 149.623 | 55.3244
|  |  | 72 | 1542.8571 | 1564.2857 | 0.0095219 | 149.058 | 149.6188 | 54.5185
|  |  | 73 | 1564.2857 | 1585.7143 | 0.0093914 | 149.0615 | 149.6148 | 53.7355
|  |  | 74 | 1585.7143 | 1607.1429 | 0.0092645 | 149.065 | 149.6108 | 52.9745
|  |  | 75 | 1607.1429 | 1628.5714 | 0.009141 | 149.0684 | 149.607 | 52.2345
|  |  | 76 | 1628.5714 | 1650 | 0.0090207 | 149.0717 | 149.6032 | 51.5147
|  |  | 77 | 1650 | 1671.4286 | 0.0089036 | 149.0749 | 149.5996 | 50.8143
|  |  | 78 | 1671.4286 | 1692.8571 | 0.0087894 | 149.078 | 149.596 | 50.1325
|  |  | 79 | 1692.8571 | 1714.2857 | 0.0086782 | 149.0811 | 149.5926 | 49.4686
|  |  | 80 | 1714.2857 | 1735.7143 | 0.0085697 | 149.084 | 149.5892 | 48.8219
|  |  | 81 | 1735.7143 | 1757.1429 | 0.0084639 | 149.087 | 149.5859 | 48.1917
|  |  | 82 | 1757.1429 | 1778.5714 | 0.0083607 | 149.0898 | 149.5827 | 47.5775
|  |  | 83 | 1778.5714 | 1800 | 0.0082599 | 149.0926 | 149.5796 | 46.9785
|  |  | 84 | 1800 | 1821.4286 | 0.0081616 | 149.0953 | 149.5765 | 46.3944
|  |  | 85 | 1821.4286 | 1842.8571 | 0.0080656 | 149.0979 | 149.5735 | 45.8244
|  |  | 86 | 1842.8571 | 1864.2857 | 0.0079718 | 149.1005 | 149.5706 | 45.2682
|  |  | 87 | 1864.2857 | 1885.7143 | 0.0078802 | 149.103 | 149.5678 | 44.7252
|  |  | 88 | 1885.7143 | 1907.1429 | 0.0077906 | 149.1055 | 149.565 | 44.195
|  |  | 89 | 1907.1429 | 1928.5714 | 0.0077031 | 149.1079 | 149.5623 | 43.6771
|  |  | 90 | 1928.5714 | 1950 | 0.0076175 | 149.1103 | 149.5596 | 43.171
|  |  | 91 | 1950 | 1971.4286 | 0.0075338 | 149.1126 | 149.557 | 42.6765
|  |  | 92 | 1971.4286 | 1992.8571 | 0.0074519 | 149.1149 | 149.5545 | 42.1931
|  |  | 93 | 1992.8571 | 2014.2857 | 0.0073718 | 149.1171 | 149.552 | 41.7204
|  |  | 94 | 2014.2857 | 2035.7143 | 0.0072934 | 149.1192 | 149.5496 | 41.2581
|  |  | 95 | 2035.7143 | 2057.1429 | 0.0072166 | 149.1214 | 149.5472 | 40.8059
|  |  | 96 | 2057.1429 | 2078.5714 | 0.0071414 | 149.1235 | 149.5449 | 40.3634
|  |  | 97 | 2078.5714 | 2100 | 0.0070678 | 149.1255 | 149.5426 | 39.9303
|  |  | 98 | 2100 | 2121.4286 | 0.0069957 | 149.1275 | 149.5403 | 39.5063
|  |  | 99 | 2121.4286 | 2142.8571 | 0.006925 | 149.1295 | 149.5382 | 39.0912
|  |  | 100 | 2142.8571 | 2164.2857 | 0.0068558 | 149.1314 | 149.536 | 38.6846
|  |  | 101 | 2164.2857 | 2185.7143 | 0.0067879 | 149.1333 | 149.5339 | 38.2864
|  |  | 102 | 2185.7143 | 2207.1429 | 0.0067213 | 149.1351 | 149.5319 | 37.8962
|  |  | 103 | 2207.1429 | 2228.5714 | 0.0066561 | 149.1369 | 149.5298 | 37.5138
|  |  | 104 | 2228.5714 | 2250 | 0.0065921 | 149.1387 | 149.5279 | 37.139
|  |  | 105 | 2250 | 2271.4286 | 0.0065293 | 149.1405 | 149.5259 | 36.7715
|  |  | 106 | 2271.4286 | 2292.8571 | 0.0064677 | 149.1422 | 149.524 | 36.4112
|  |  | 107 | 2292.8571 | 2314.2857 | 0.0064072 | 149.1439 | 149.5221 | 36.0579
|  |  | 108 | 2314.2857 | 2335.7143 | 0.0063479 | 149.1455 | 149.5203 | 35.7113
|  |  | 109 | 2335.7143 | 2357.1429 | 0.0062897 | 149.1471 | 149.5185 | 35.3712
|  |  | 110 | 2357.1429 | 2378.5714 | 0.0062325 | 149.1487 | 149.5168 | 35.0375
|  |  | 111 | 2378.5714 | 2400 | 0.0061764 | 149.1503 | 149.515 | 34.71
|  |  | 112 | 2400 | 2421.4286 | 0.0061212 | 149.1518 | 149.5133 | 34.3885
|  |  | 113 | 2421.4286 | 2442.8571 | 0.006067 | 149.1533 | 149.5116 | 34.0729
|  |  | 114 | 2442.8571 | 2464.2857 | 0.0060138 | 149.1548 | 149.51 | 33.7629
|  |  | 115 | 2464.2857 | 2485.7143 | 0.0059615 | 149.1563 | 149.5084 | 33.4586
|  |  | 116 | 2485.7143 | 2507.1429 | 0.0059101 | 149.1577 | 149.5068 | 33.1596
|  |  | 117 | 2507.1429 | 2528.5714 | 0.0058596 | 149.1591 | 149.5052 | 32.8659
|  |  | 118 | 2528.5714 | 2550 | 0.00581 | 149.1605 | 149.5037 | 32.5773
|  |  | 119 | 2550 | 2571.4286 | 0.0057611 | 149.1619 | 149.5022 | 32.2937
|  |  | 120 | 2571.4286 | 2592.8571 | 0.0057131 | 149.1632 | 149.5007 | 32.0149
|  |  | 121 | 2592.8571 | 2614.2857 | 0.0056659 | 149.1645 | 149.4993 | 31.7409
|  |  | 122 | 2614.2857 | 2635.7143 | 0.0056195 | 149.1658 | 149.4978 | 31.4715
|  |  | 123 | 2635.7143 | 2657.1429 | 0.0055738 | 149.1671 | 149.4964 | 31.2066
|  |  | 124 | 2657.1429 | 2678.5714 | 0.0055288 | 149.1684 | 149.495 | 30.9461
|  |  | 125 | 2678.5714 | 2700 | 0.0054846 | 149.1696 | 149.4937 | 30.6899
|  |  | 126 | 2700 | 2721.4286 | 0.0054411 | 149.1708 | 149.4923 | 30.4379
|  |  | 127 | 2721.4286 | 2742.8571 | 0.0053982 | 149.172 | 149.491 | 30.1899
|  |  | 128 | 2742.8571 | 2764.2857 | 0.0053561 | 149.1732 | 149.4897 | 29.946
|  |  | 129 | 2764.2857 | 2785.7143 | 0.0053145 | 149.1744 | 149.4884 | 29.7059
|  |  | 130 | 2785.7143 | 2807.1429 | 0.0052737 | 149.1755 | 149.4872 | 29.4696
|  |  | 131 | 2807.1429 | 2828.5714 | 0.0052334 | 149.1767 | 149.4859 | 29.237
|  |  | 132 | 2828.5714 | 2850 | 0.0051938 | 149.1778 | 149.4847 | 29.008
|  |  | 133 | 2850 | 2871.4286 | 0.0051547 | 149.1789 | 149.4835 | 28.7826
|  |  | 134 | 2871.4286 | 2892.8571 | 0.0051162 | 149.18 | 149.4823 | 28.5606
|  |  | 135 | 2892.8571 | 2914.2857 | 0.0050783 | 149.181 | 149.4812 | 28.342
|  |  | 136 | 2914.2857 | 2935.7143 | 0.005041 | 149.1821 | 149.48 | 28.1267
|  |  | 137 | 2935.7143 | 2957.1429 | 0.0050042 | 149.1831 | 149.4789 | 27.9147
|  |  | 138 | 2957.1429 | 2978.5714 | 0.0049679 | 149.1841 | 149.4778 | 27.7057
|  |  | 139 | 2978.5714 | 3000 | 0.0049322 | 149.1851 | 149.4767 | 27.4999
|  |  | 140 | 3000 | 3021.4286 | 0.004897 | 149.1861 | 149.4756 | 27.2971
|  |  | 141 | 3021.4286 | 3042.8571 | 0.0048622 | 149.1871 | 149.4745 | 27.0972
|  |  | 142 | 3042.8571 | 3064.2857 | 0.004828 | 149.1881 | 149.4735 | 26.9002
|  |  | 143 | 3064.2857 | 3085.7143 | 0.0047942 | 149.189 | 149.4724 | 26.7061
|  |  | 144 | 3085.7143 | 3107.1429 | 0.0047609 | 149.19 | 149.4714 | 26.5147
|  |  | 145 | 3107.1429 | 3128.5714 | 0.0047281 | 149.1909 | 149.4704 | 26.326
|  |  | 146 | 3128.5714 | 3150 | 0.0046957 | 149.1918 | 149.4694 | 26.14
|  |  | 147 | 3150 | 3171.4286 | 0.0046638 | 149.1927 | 149.4684 | 25.9566
|  |  | 148 | 3171.4286 | 3192.8571 | 0.0046323 | 149.1936 | 149.4675 | 25.7757
|  |  | 149 | 3192.8571 | 3214.2857 | 0.0046012 | 149.1945 | 149.4665 | 25.5973
|  |  | 150 | 3214.2857 | 3235.7143 | 0.0045705 | 149.1953 | 149.4656 | 25.4213
|  |  | 151 | 3235.7143 | 3257.1429 | 0.0045402 | 149.1962 | 149.4646 | 25.2477
|  |  | 152 | 3257.1429 | 3278.5714 | 0.0045104 | 149.197 | 149.4637 | 25.0765
|  |  | 153 | 3278.5714 | 3300 | 0.0044809 | 149.1979 | 149.4628 | 24.9075
|  |  | 154 | 3300 | 3321.4286 | 0.0044518 | 149.1987 | 149.4619 | 24.7408
|  |  | 155 | 3321.4286 | 3342.8571 | 0.0044231 | 149.1995 | 149.461 | 24.5763
|  |  | 156 | 3342.8571 | 3364.2857 | 0.0043947 | 149.2003 | 149.4602 | 24.414
|  |  | 157 | 3364.2857 | 3385.7143 | 0.0043667 | 149.2011 | 149.4593 | 24.2538
|  |  | 158 | 3385.7143 | 3407.1429 | 0.0043391 | 149.2019 | 149.4585 | 24.0957
|  |  | 159 | 3407.1429 | 3428.5714 | 0.0043118 | 149.2026 | 149.4576 | 23.9396
|  |  | 160 | 3428.5714 | 3450 | 0.0042848 | 149.2034 | 149.4568 | 23.7855
|  |  | 161 | 3450 | 3471.4286 | 0.0042582 | 149.2041 | 149.456 | 23.6333
|  |  | 162 | 3471.4286 | 3492.8571 | 0.0042319 | 149.2049 | 149.4552 | 23.4831
|  |  | 163 | 3492.8571 | 3514.2857 | 0.004206 | 149.2056 | 149.4544 | 23.3348
|  |  | 164 | 3514.2857 | 3535.7143 | 0.0041803 | 149.2064 | 149.4536 | 23.1883
|  |  | 165 | 3535.7143 | 3557.1429 | 0.004155 | 149.2071 | 149.4528 | 23.0436
|  |  | 166 | 3557.1429 | 3578.5714 | 0.00413 | 149.2078 | 149.452 | 22.9008
|  |  | 167 | 3578.5714 | 3600 | 0.0041052 | 149.2085 | 149.4513 | 22.7596
|  |  | 168 | 3600 |  | 0.0040808 | 149.2092 |  | 0
Note on I3: Bob Glicksman: Equation 6-5
Note on J3: Bob Glicksman: Equation 6-4
Note on K3: Bob Glicksman: Euation 6-2a
Note on L3: Bob Glicksman: Equation 6-1

## Cold Tank - Xchange
CONSTANTS |  |  | DYNAMIC TEMPERATURE VARIATION IN COLD TANK
One gallon of water weighs: | 8.34 | lbs
One gallon of water comprises: | 0.13368 | cu-ft | Time (min) | Cold Tank Temp (degF) | New Cold Tank Temp (degF) | Ferment Tank Mass thru Cold Tank (lb) | Ferment Tank Volume thru Cold Tank (gal) | Ferment Tank Mass bypass Cold Tank (gal) | Ferment Tank Volume bypass Cold Tank (gal) | Ferment Tank Volume, total (gal) | Ferment Tank Temp thru Cold Tank (degF) | Ferment Tank Temp bypass Cold Tank (degF) | Ferment Tank temp (deg F)
Minutes per Hour | 60 | minutes
|  |  | 1 | 40 | 40.5212 | 183.7719 | 22.035 | 98.9541 | 11.865 | 33.9 | 40.5212 | 135.1375 | 73.6369
INPUT VALUES AND BASIC CALCS |  |  | 2 | 40.5212 | 41.0396 | 367.5438 | 44.07 | 197.9082 | 23.73 | 67.8 | 40.7804 | 135.1375 | 73.8054
one refrigeration ton = | 3.5169 | Kw | 3 | 41.0396 | 41.5551 | 551.3157 | 66.105 | 296.8623 | 35.595 | 101.7 | 41.0386 | 135.1375 | 73.9732
height of cylindrical tank: | 7 | ft | 4 | 41.5551 | 42.0678 | 735.0876 | 88.14 | 395.8164 | 47.46 | 135.6 | 41.2959 | 135.1375 | 74.1405
diameter of cylindrical tank: | 12 | ft | 5 | 42.0678 | 42.5777 | 918.8595 | 110.175 | 494.7705 | 59.325 | 169.5 | 41.5523 | 135.1375 | 74.3071
Volume of Wort to Transfer: | 4068 | gal | 6 | 42.5777 | 43.0848 | 1102.6314 | 132.21 | 593.7246 | 71.19 | 203.4 | 41.8077 | 135.1375 | 74.4731
Temperature of Wort: | 135.1375 | deg F | 7 | 43.0848 | 43.5891 | 1286.4033 | 154.245 | 692.6787 | 83.055 | 237.3 | 42.0622 | 135.1375 | 74.6386
Desired ending temperature: | 90 | deg F | 8 | 43.5891 | 44.0907 | 1470.1752 | 176.28 | 791.6328 | 94.92 | 271.2 | 42.3157 | 135.1375 | 74.8034
Total transfer time | 2 | hours | 9 | 44.0907 | 44.5895 | 1653.9471 | 198.315 | 890.5869 | 106.785 | 305.1 | 42.5684 | 135.1375 | 74.9676
Volume of water/brine in Cold Tank: | 4000 | gal | 10 | 44.5895 | 45.0855 | 1837.719 | 220.35 | 989.541 | 118.65 | 339 | 42.8201 | 135.1375 | 75.1312
Initial temperature of Cold Tank Water/Brine: | 40 | degF | 11 | 45.0855 | 45.5789 | 2021.4909 | 242.385 | 1088.4951 | 130.515 | 372.9 | 43.0709 | 135.1375 | 75.2942
COP of refrigeration unit: | 2 |  | 12 | 45.5789 | 46.0695 | 2205.2628 | 264.42 | 1187.4492 | 142.38 | 406.8 | 43.3208 | 135.1375 | 75.4566
Volume of cylindrical tank = | 791.6813 | cu-ft | 13 | 46.0695 | 46.5575 | 2389.0347 | 286.455 | 1286.4033 | 154.245 | 440.7 | 43.5698 | 135.1375 | 75.6185
Volume of cylindrical tank = | 5922.2124 | gallons | 14 | 46.5575 | 47.0428 | 2572.8066 | 308.49 | 1385.3574 | 166.11 | 474.6 | 43.8178 | 135.1375 | 75.7797
Flow rate of wort (total) = | 33.9 | gal/minute | 15 | 47.0428 | 47.5254 | 2756.5785 | 330.525 | 1484.3115 | 177.975 | 508.5 | 44.065 | 135.1375 | 75.9404
% Flow rate of wort through cold tank = | 65% |  | 16 | 47.5254 | 48.0054 | 2940.3504 | 352.56 | 1583.2656 | 189.84 | 542.4 | 44.3113 | 135.1375 | 76.1005
Mass of cold tank water/brine = | 33360 | lbs | 17 | 48.0054 | 48.4828 | 3124.1223 | 374.595 | 1682.2197 | 201.705 | 576.3 | 44.5567 | 135.1375 | 76.26
Mass of wort thru Cold Tank, per minute = | 183.7719 | lbs | 18 | 48.4828 | 48.9575 | 3307.8942 | 396.63 | 1781.1738 | 213.57 | 610.2 | 44.8012 | 135.1375 | 76.4189
Mass of wort bypass Cold Tank, per minute = | 98.9541 | lbs | 19 | 48.9575 | 49.4297 | 3491.6661 | 418.665 | 1880.1279 | 225.435 | 644.1 | 45.0448 | 135.1375 | 76.5772
Final temperature of wort in ferment tank = | 89.9773 | deg F | 20 | 49.4297 | 49.8992 | 3675.438 | 440.7 | 1979.082 | 237.3 | 678 | 45.2875 | 135.1375 | 76.735
Final temperature of cold tank water/brine = | 85.6569 | deg F | 21 | 49.8992 | 50.3662 | 3859.2099 | 462.735 | 2078.0361 | 249.165 | 711.9 | 45.5293 | 135.1375 | 76.8922
Mass of cold tank water/brine = | 33360 | lbs | 22 | 50.3662 | 50.8306 | 4042.9818 | 484.77 | 2176.9902 | 261.03 | 745.8 | 45.7703 | 135.1375 | 77.0488
Heat to remove over the next week = | 1523114.0397 | BTU | 23 | 50.8306 | 51.2925 | 4226.7537 | 506.805 | 2275.9443 | 272.895 | 779.7 | 46.0104 | 135.1375 | 77.2049
Heat to remove per hour over the week = | 9175.3858 | BTU/hr | 24 | 51.2925 | 51.7519 | 4410.5256 | 528.84 | 2374.8984 | 284.76 | 813.6 | 46.2496 | 135.1375 | 77.3604
|  |  | 25 | 51.7519 | 52.2087 | 4594.2975 | 550.875 | 2473.8525 | 296.625 | 847.5 | 46.488 | 135.1375 | 77.5153
check: heat lost in wort = | 1532157.3708 |  | 26 | 52.2087 | 52.663 | 4778.0694 | 572.91 | 2572.8066 | 308.49 | 881.4 | 46.7255 | 135.1375 | 77.6697
|  |  | 27 | 52.663 | 53.1149 | 4961.8413 | 594.945 | 2671.7607 | 320.355 | 915.3 | 46.9621 | 135.1375 | 77.8235
|  |  | 28 | 53.1149 | 53.5642 | 5145.6132 | 616.98 | 2770.7148 | 332.22 | 949.2 | 47.1979 | 135.1375 | 77.9768
|  |  | 29 | 53.5642 | 54.0111 | 5329.3851 | 639.015 | 2869.6689 | 344.085 | 983.1 | 47.4329 | 135.1375 | 78.1295
|  |  | 30 | 54.0111 | 54.4556 | 5513.157 | 661.05 | 2968.623 | 355.95 | 1017 | 47.667 | 135.1375 | 78.2817
|  |  | 31 | 54.4556 | 54.8976 | 5696.9289 | 683.085 | 3067.5771 | 367.815 | 1050.9 | 47.9002 | 135.1375 | 78.4333
|  |  | 32 | 54.8976 | 55.3372 | 5880.7008 | 705.12 | 3166.5312 | 379.68 | 1084.8 | 48.1326 | 135.1375 | 78.5843
|  |  | 33 | 55.3372 | 55.7744 | 6064.4727 | 727.155 | 3265.4853 | 391.545 | 1118.7 | 48.3642 | 135.1375 | 78.7348
|  |  | 34 | 55.7744 | 56.2092 | 6248.2446 | 749.19 | 3364.4394 | 403.41 | 1152.6 | 48.5949 | 135.1375 | 78.8848
|  |  | 35 | 56.2092 | 56.6416 | 6432.0165 | 771.225 | 3463.3935 | 415.275 | 1186.5 | 48.8248 | 135.1375 | 79.0343
|  |  | 36 | 56.6416 | 57.0717 | 6615.7884 | 793.26 | 3562.3476 | 427.14 | 1220.4 | 49.0539 | 135.1375 | 79.1832
|  |  | 37 | 57.0717 | 57.4994 | 6799.5603 | 815.295 | 3661.3017 | 439.005 | 1254.3 | 49.2822 | 135.1375 | 79.3315
|  |  | 38 | 57.4994 | 57.9247 | 6983.3322 | 837.33 | 3760.2558 | 450.87 | 1288.2 | 49.5096 | 135.1375 | 79.4794
|  |  | 39 | 57.9247 | 58.3477 | 7167.1041 | 859.365 | 3859.2099 | 462.735 | 1322.1 | 49.7362 | 135.1375 | 79.6267
|  |  | 40 | 58.3477 | 58.7684 | 7350.876 | 881.4 | 3958.164 | 474.6 | 1356 | 49.962 | 135.1375 | 79.7734
|  |  | 41 | 58.7684 | 59.1868 | 7534.6479 | 903.435 | 4057.1181 | 486.465 | 1389.9 | 50.187 | 135.1375 | 79.9197
|  |  | 42 | 59.1868 | 59.6029 | 7718.4198 | 925.47 | 4156.0722 | 498.33 | 1423.8 | 50.4112 | 135.1375 | 80.0654
|  |  | 43 | 59.6029 | 60.0167 | 7902.1917 | 947.505 | 4255.0263 | 510.195 | 1457.7 | 50.6346 | 135.1375 | 80.2106
|  |  | 44 | 60.0167 | 60.4283 | 8085.9636 | 969.54 | 4353.9804 | 522.06 | 1491.6 | 50.8572 | 135.1375 | 80.3553
|  |  | 45 | 60.4283 | 60.8376 | 8269.7355 | 991.575 | 4452.9345 | 533.925 | 1525.5 | 51.079 | 135.1375 | 80.4995
|  |  | 46 | 60.8376 | 61.2447 | 8453.5074 | 1013.61 | 4551.8886 | 545.79 | 1559.4 | 51.2999 | 135.1375 | 80.6431
|  |  | 47 | 61.2447 | 61.6495 | 8637.2793 | 1035.645 | 4650.8427 | 557.655 | 1593.3 | 51.5202 | 135.1375 | 80.7862
|  |  | 48 | 61.6495 | 62.0521 | 8821.0512 | 1057.68 | 4749.7968 | 569.52 | 1627.2 | 51.7396 | 135.1375 | 80.9289
|  |  | 49 | 62.0521 | 62.4525 | 9004.8231 | 1079.715 | 4848.7509 | 581.385 | 1661.1 | 51.9582 | 135.1375 | 81.071
|  |  | 50 | 62.4525 | 62.8507 | 9188.595 | 1101.75 | 4947.705 | 593.25 | 1695 | 52.176 | 135.1375 | 81.2126
|  |  | 51 | 62.8507 | 63.2467 | 9372.3669 | 1123.785 | 5046.6591 | 605.115 | 1728.9 | 52.3931 | 135.1375 | 81.3537
|  |  | 52 | 63.2467 | 63.6406 | 9556.1388 | 1145.82 | 5145.6132 | 616.98 | 1762.8 | 52.6094 | 135.1375 | 81.4943
|  |  | 53 | 63.6406 | 64.0323 | 9739.9107 | 1167.855 | 5244.5673 | 628.845 | 1796.7 | 52.8249 | 135.1375 | 81.6343
|  |  | 54 | 64.0323 | 64.4218 | 9923.6826 | 1189.89 | 5343.5214 | 640.71 | 1830.6 | 53.0397 | 135.1375 | 81.7739
|  |  | 55 | 64.4218 | 64.8093 | 10107.4545 | 1211.925 | 5442.4755 | 652.575 | 1864.5 | 53.2537 | 135.1375 | 81.913
|  |  | 56 | 64.8093 | 65.1946 | 10291.2264 | 1233.96 | 5541.4296 | 664.44 | 1898.4 | 53.4669 | 135.1375 | 82.0516
|  |  | 57 | 65.1946 | 65.5778 | 10474.9983 | 1255.995 | 5640.3837 | 676.305 | 1932.3 | 53.6794 | 135.1375 | 82.1897
|  |  | 58 | 65.5778 | 65.9588 | 10658.7702 | 1278.03 | 5739.3378 | 688.17 | 1966.2 | 53.8911 | 135.1375 | 82.3274
|  |  | 59 | 65.9588 | 66.3378 | 10842.5421 | 1300.065 | 5838.2919 | 700.035 | 2000.1 | 54.1021 | 135.1375 | 82.4645
|  |  | 60 | 66.3378 | 66.7148 | 11026.314 | 1322.1 | 5937.246 | 711.9 | 2034 | 54.3123 | 135.1375 | 82.6011
|  |  | 61 | 66.7148 | 67.0896 | 11210.0859 | 1344.135 | 6036.2001 | 723.765 | 2067.9 | 54.5217 | 135.1375 | 82.7373
|  |  | 62 | 67.0896 | 67.4624 | 11393.8578 | 1366.17 | 6135.1542 | 735.63 | 2101.8 | 54.7305 | 135.1375 | 82.8729
|  |  | 63 | 67.4624 | 67.8332 | 11577.6297 | 1388.205 | 6234.1083 | 747.495 | 2135.7 | 54.9384 | 135.1375 | 83.0081
|  |  | 64 | 67.8332 | 68.2019 | 11761.4016 | 1410.24 | 6333.0624 | 759.36 | 2169.6 | 55.1457 | 135.1375 | 83.1428
|  |  | 65 | 68.2019 | 68.5686 | 11945.1735 | 1432.275 | 6432.0165 | 771.225 | 2203.5 | 55.3522 | 135.1375 | 83.2771
|  |  | 66 | 68.5686 | 68.9333 | 12128.9454 | 1454.31 | 6530.9706 | 783.09 | 2237.4 | 55.558 | 135.1375 | 83.4108
|  |  | 67 | 68.9333 | 69.296 | 12312.7173 | 1476.345 | 6629.9247 | 794.955 | 2271.3 | 55.763 | 135.1375 | 83.5441
|  |  | 68 | 69.296 | 69.6568 | 12496.4892 | 1498.38 | 6728.8788 | 806.82 | 2305.2 | 55.9673 | 135.1375 | 83.6769
|  |  | 69 | 69.6568 | 70.0155 | 12680.2611 | 1520.415 | 6827.8329 | 818.685 | 2339.1 | 56.1709 | 135.1375 | 83.8092
|  |  | 70 | 70.0155 | 70.3723 | 12864.033 | 1542.45 | 6926.787 | 830.55 | 2373 | 56.3738 | 135.1375 | 83.9411
|  |  | 71 | 70.3723 | 70.7271 | 13047.8049 | 1564.485 | 7025.7411 | 842.415 | 2406.9 | 56.576 | 135.1375 | 84.0725
|  |  | 72 | 70.7271 | 71.08 | 13231.5768 | 1586.52 | 7124.6952 | 854.28 | 2440.8 | 56.7774 | 135.1375 | 84.2034
|  |  | 73 | 71.08 | 71.4309 | 13415.3487 | 1608.555 | 7223.6493 | 866.145 | 2474.7 | 56.9781 | 135.1375 | 84.3339
|  |  | 74 | 71.4309 | 71.7799 | 13599.1206 | 1630.59 | 7322.6034 | 878.01 | 2508.6 | 57.1782 | 135.1375 | 84.4639
|  |  | 75 | 71.7799 | 72.127 | 13782.8925 | 1652.625 | 7421.5575 | 889.875 | 2542.5 | 57.3775 | 135.1375 | 84.5935
|  |  | 76 | 72.127 | 72.4723 | 13966.6644 | 1674.66 | 7520.5116 | 901.74 | 2576.4 | 57.5761 | 135.1375 | 84.7226
|  |  | 77 | 72.4723 | 72.8156 | 14150.4363 | 1696.695 | 7619.4657 | 913.605 | 2610.3 | 57.774 | 135.1375 | 84.8512
|  |  | 78 | 72.8156 | 73.157 | 14334.2082 | 1718.73 | 7718.4198 | 925.47 | 2644.2 | 57.9712 | 135.1375 | 84.9794
|  |  | 79 | 73.157 | 73.4966 | 14517.9801 | 1740.765 | 7817.3739 | 937.335 | 2678.1 | 58.1678 | 135.1375 | 85.1072
|  |  | 80 | 73.4966 | 73.8343 | 14701.752 | 1762.8 | 7916.328 | 949.2 | 2712 | 58.3636 | 135.1375 | 85.2345
|  |  | 81 | 73.8343 | 74.1701 | 14885.5239 | 1784.835 | 8015.2821 | 961.065 | 2745.9 | 58.5587 | 135.1375 | 85.3613
|  |  | 82 | 74.1701 | 74.5041 | 15069.2958 | 1806.87 | 8114.2362 | 972.93 | 2779.8 | 58.7532 | 135.1375 | 85.4877
|  |  | 83 | 74.5041 | 74.8363 | 15253.0677 | 1828.905 | 8213.1903 | 984.795 | 2813.7 | 58.947 | 135.1375 | 85.6137
|  |  | 84 | 74.8363 | 75.1667 | 15436.8396 | 1850.94 | 8312.1444 | 996.66 | 2847.6 | 59.1401 | 135.1375 | 85.7392
|  |  | 85 | 75.1667 | 75.4952 | 15620.6115 | 1872.975 | 8411.0985 | 1008.525 | 2881.5 | 59.3325 | 135.1375 | 85.8642
|  |  | 86 | 75.4952 | 75.822 | 15804.3834 | 1895.01 | 8510.0526 | 1020.39 | 2915.4 | 59.5242 | 135.1375 | 85.9889
|  |  | 87 | 75.822 | 76.147 | 15988.1553 | 1917.045 | 8609.0067 | 1032.255 | 2949.3 | 59.7153 | 135.1375 | 86.1131
|  |  | 88 | 76.147 | 76.4701 | 16171.9272 | 1939.08 | 8707.9608 | 1044.12 | 2983.2 | 59.9057 | 135.1375 | 86.2368
|  |  | 89 | 76.4701 | 76.7916 | 16355.6991 | 1961.115 | 8806.9149 | 1055.985 | 3017.1 | 60.0954 | 135.1375 | 86.3601
|  |  | 90 | 76.7916 | 77.1112 | 16539.471 | 1983.15 | 8905.869 | 1067.85 | 3051 | 60.2845 | 135.1375 | 86.483
|  |  | 91 | 77.1112 | 77.4291 | 16723.2429 | 2005.185 | 9004.8231 | 1079.715 | 3084.9 | 60.4729 | 135.1375 | 86.6055
|  |  | 92 | 77.4291 | 77.7453 | 16907.0148 | 2027.22 | 9103.7772 | 1091.58 | 3118.8 | 60.6606 | 135.1375 | 86.7275
|  |  | 93 | 77.7453 | 78.0597 | 17090.7867 | 2049.255 | 9202.7313 | 1103.445 | 3152.7 | 60.8477 | 135.1375 | 86.8491
|  |  | 94 | 78.0597 | 78.3724 | 17274.5586 | 2071.29 | 9301.6854 | 1115.31 | 3186.6 | 61.0341 | 135.1375 | 86.9703
|  |  | 95 | 78.3724 | 78.6834 | 17458.3305 | 2093.325 | 9400.6395 | 1127.175 | 3220.5 | 61.2199 | 135.1375 | 87.0911
|  |  | 96 | 78.6834 | 78.9927 | 17642.1024 | 2115.36 | 9499.5936 | 1139.04 | 3254.4 | 61.405 | 135.1375 | 87.2114
|  |  | 97 | 78.9927 | 79.3003 | 17825.8743 | 2137.395 | 9598.5477 | 1150.905 | 3288.3 | 61.5895 | 135.1375 | 87.3313
|  |  | 98 | 79.3003 | 79.6062 | 18009.6462 | 2159.43 | 9697.5018 | 1162.77 | 3322.2 | 61.7734 | 135.1375 | 87.4508
|  |  | 99 | 79.6062 | 79.9104 | 18193.4181 | 2181.465 | 9796.4559 | 1174.635 | 3356.1 | 61.9566 | 135.1375 | 87.5699
|  |  | 100 | 79.9104 | 80.213 | 18377.19 | 2203.5 | 9895.41 | 1186.5 | 3390 | 62.1391 | 135.1375 | 87.6886
|  |  | 101 | 80.213 | 80.5139 | 18560.9619 | 2225.535 | 9994.3641 | 1198.365 | 3423.9 | 62.3211 | 135.1375 | 87.8068
|  |  | 102 | 80.5139 | 80.8132 | 18744.7338 | 2247.57 | 10093.3182 | 1210.23 | 3457.8 | 62.5024 | 135.1375 | 87.9247
|  |  | 103 | 80.8132 | 81.1108 | 18928.5057 | 2269.605 | 10192.2723 | 1222.095 | 3491.7 | 62.683 | 135.1375 | 88.0421
|  |  | 104 | 81.1108 | 81.4068 | 19112.2776 | 2291.64 | 10291.2264 | 1233.96 | 3525.6 | 62.8631 | 135.1375 | 88.1591
|  |  | 105 | 81.4068 | 81.7011 | 19296.0495 | 2313.675 | 10390.1805 | 1245.825 | 3559.5 | 63.0425 | 135.1375 | 88.2757
|  |  | 106 | 81.7011 | 81.9939 | 19479.8214 | 2335.71 | 10489.1346 | 1257.69 | 3593.4 | 63.2213 | 135.1375 | 88.392
|  |  | 107 | 81.9939 | 82.285 | 19663.5933 | 2357.745 | 10588.0887 | 1269.555 | 3627.3 | 63.3994 | 135.1375 | 88.5078
|  |  | 108 | 82.285 | 82.5746 | 19847.3652 | 2379.78 | 10687.0428 | 1281.42 | 3661.2 | 63.577 | 135.1375 | 88.6232
|  |  | 109 | 82.5746 | 82.8626 | 20031.1371 | 2401.815 | 10785.9969 | 1293.285 | 3695.1 | 63.7539 | 135.1375 | 88.7382
|  |  | 110 | 82.8626 | 83.149 | 20214.909 | 2423.85 | 10884.951 | 1305.15 | 3729 | 63.9302 | 135.1375 | 88.8528
|  |  | 111 | 83.149 | 83.4338 | 20398.6809 | 2445.885 | 10983.9051 | 1317.015 | 3762.9 | 64.1059 | 135.1375 | 88.967
|  |  | 112 | 83.4338 | 83.717 | 20582.4528 | 2467.92 | 11082.8592 | 1328.88 | 3796.8 | 64.281 | 135.1375 | 89.0808
|  |  | 113 | 83.717 | 83.9987 | 20766.2247 | 2489.955 | 11181.8133 | 1340.745 | 3830.7 | 64.4555 | 135.1375 | 89.1942
|  |  | 114 | 83.9987 | 84.2789 | 20949.9966 | 2511.99 | 11280.7674 | 1352.61 | 3864.6 | 64.6294 | 135.1375 | 89.3073
|  |  | 115 | 84.2789 | 84.5575 | 21133.7685 | 2534.025 | 11379.7215 | 1364.475 | 3898.5 | 64.8027 | 135.1375 | 89.4199
|  |  | 116 | 84.5575 | 84.8347 | 21317.5404 | 2556.06 | 11478.6756 | 1376.34 | 3932.4 | 64.9754 | 135.1375 | 89.5321
|  |  | 117 | 84.8347 | 85.1102 | 21501.3123 | 2578.095 | 11577.6297 | 1388.205 | 3966.3 | 65.1475 | 135.1375 | 89.644
|  |  | 118 | 85.1102 | 85.3843 | 21685.0842 | 2600.13 | 11676.5838 | 1400.07 | 4000.2 | 65.319 | 135.1375 | 89.7555
|  |  | 119 | 85.3843 | 85.6569 | 21868.8561 | 2622.165 | 11775.5379 | 1411.935 | 4034.1 | 65.4899 | 135.1375 | 89.8666
|  |  | 120 | 85.6569 | 85.928 | 22052.628 | 2644.2 | 11874.492 | 1423.8 | 4068 | 65.6602 | 135.1375 | 89.9773
Note on B7: Bob Glicksman: http://www.rapidtables.com/convert/power/ton-to-kw.htm
Note on B10: Bob Glicksman: max volume: 3600 gal stillage + 13% * 3600 (max alcohol) = 4068 gallons of wort.
Note on A16: Bob Glicksman: http://en.wikipedia.org/wiki/Coefficient_of_performance

## Cold Tank - Cool
CONSTANTS |  |  | COLD TANK HEAT LOSS OVER TIME
One gallon of water weighs: | 8.34 | lbs
One gallon of water comprises: | 0.13368 | cu-ft | Time (hr) | Temp of Cold Tank (deg F) | BTU loss in one hour due to conduction | BTU loss in one hour due to refrigeration | Total BTU loss over one hour | Temp drop in cold tank per hr (deg F)
Hours for cooldown in a week: | 166 | hours | 0 | 85.6569 | -106.4253 | 9960 | 9853.5747 | 0.29537
BTU per ton of refrigeration: | 12000 | BTU | 1 | 85.3615 | -113.6632 | 9960 | 9846.3368 | 0.29515
one refrigeration ton = | 3.5169 | Kw | 2 | 85.0664 | -120.8957 | 9960 | 9839.1043 | 0.29494
|  |  | 3 | 84.7714 | -128.123 | 9960 | 9831.877 | 0.29472
INPUT VALUES AND BASIC CALCS |  |  | 4 | 84.4767 | -135.345 | 9960 | 9824.655 | 0.2945
R-value: | 20 | (sq-ft * deltaT*hr)/BTU | 5 | 84.1822 | -142.5616 | 9960 | 9817.4384 | 0.29429
height of cylindrical tank: | 7 | ft | 6 | 83.8879 | -149.773 | 9960 | 9810.227 | 0.29407
diameter of cylindrical tank: | 12 | ft | 7 | 83.5938 | -156.979 | 9960 | 9803.021 | 0.29386
Initial temperature of cold tank T(0): | 85.6569 | deg F | 8 | 83.3 | -164.1798 | 9960 | 9795.8202 | 0.29364
Ambient Temperature: | 90 | deg F | 9 | 83.0064 | -171.3752 | 9960 | 9788.6248 | 0.29342
Desired Final Temperature of Cold Tank T(f): | 40 | deg F | 10 | 82.7129 | -178.5654 | 9960 | 9781.4346 | 0.29321
Volume of water/brine in cold tank: | 4000 | gallons | 11 | 82.4197 | -185.7503 | 9960 | 9774.2497 | 0.29299
COP of refrigeration unit: | 2 |  | 12 | 82.1267 | -192.93 | 9960 | 9767.07 | 0.29278
Volume of cylindrical tank = | 791.6813 | cu-ft | 13 | 81.834 | -200.1043 | 9960 | 9759.8957 | 0.29256
Volume of cylindrical tank = | 5922.2124 | gallons | 14 | 81.5414 | -207.2734 | 9960 | 9752.7266 | 0.29235
Surface area of tank (top/bottom) = | 113.0973 | sq-ft | 15 | 81.249 | -214.4372 | 9960 | 9745.5628 | 0.29213
Surface area of tank (side) = | 263.8938 | sq-ft | 16 | 80.9569 | -221.5958 | 9960 | 9738.4042 | 0.29192
Total surface area of tank = | 490.0885 | sq-ft | 17 | 80.665 | -228.7491 | 9960 | 9731.2509 | 0.2917
A*h = A/R = | 24.5044 | BTU/(deltaT * hr) | 18 | 80.3733 | -235.8971 | 9960 | 9724.1029 | 0.29149
"k" = | 0.00073455 | deg F/(deltaT * hr) | 19 | 80.0818 | -243.0399 | 9960 | 9716.9601 | 0.29128
Mass of water/brine in cold tank = | 33360 | lbs | 20 | 79.7905 | -250.1774 | 9960 | 9709.8226 | 0.29106
Tons of refrigeration = | 0.83 | tons | 21 | 79.4995 | -257.3097 | 9960 | 9702.6903 | 0.29085
BTU per hour removed by refrigeration = | 9960 | BTU | 22 | 79.2086 | -264.4368 | 9960 | 9695.5632 | 0.29063
Refrigeration power requirement = | 1.4595 | Kw | 23 | 78.918 | -271.5586 | 9960 | 9688.4414 | 0.29042
Refrigeration energy requirement = | 242.276 | KwH | 24 | 78.6276 | -278.6752 | 9960 | 9681.3248 | 0.29021
Gallons of EtOH equivalent to electricty = | 10.8774 | gal | 25 | 78.3373 | -285.7866 | 9960 | 9674.2134 | 0.28999
Final Temperature of Cold Tank = | 39.4808 | deg F | 26 | 78.0474 | -292.8928 | 9960 | 9667.1072 | 0.28978
|  |  | 27 | 77.7576 | -299.9937 | 9960 | 9660.0063 | 0.28957
|  |  | 28 | 77.468 | -307.0894 | 9960 | 9652.9106 | 0.28936
|  |  | 29 | 77.1786 | -314.1799 | 9960 | 9645.8201 | 0.28914
|  |  | 30 | 76.8895 | -321.2652 | 9960 | 9638.7348 | 0.28893
|  |  | 31 | 76.6006 | -328.3453 | 9960 | 9631.6547 | 0.28872
|  |  | 32 | 76.3119 | -335.4201 | 9960 | 9624.5799 | 0.28851
|  |  | 33 | 76.0233 | -342.4898 | 9960 | 9617.5102 | 0.28829
|  |  | 34 | 75.7351 | -349.5543 | 9960 | 9610.4457 | 0.28808
|  |  | 35 | 75.447 | -356.6136 | 9960 | 9603.3864 | 0.28787
|  |  | 36 | 75.1591 | -363.6677 | 9960 | 9596.3323 | 0.28766
|  |  | 37 | 74.8714 | -370.7167 | 9960 | 9589.2833 | 0.28745
|  |  | 38 | 74.584 | -377.7604 | 9960 | 9582.2396 | 0.28724
|  |  | 39 | 74.2968 | -384.799 | 9960 | 9575.201 | 0.28703
|  |  | 40 | 74.0097 | -391.8325 | 9960 | 9568.1675 | 0.28682
|  |  | 41 | 73.7229 | -398.8607 | 9960 | 9561.1393 | 0.2866
|  |  | 42 | 73.4363 | -405.8838 | 9960 | 9554.1162 | 0.28639
|  |  | 43 | 73.1499 | -412.9017 | 9960 | 9547.0983 | 0.28618
|  |  | 44 | 72.8637 | -419.9145 | 9960 | 9540.0855 | 0.28597
|  |  | 45 | 72.5778 | -426.9221 | 9960 | 9533.0779 | 0.28576
|  |  | 46 | 72.292 | -433.9246 | 9960 | 9526.0754 | 0.28555
|  |  | 47 | 72.0064 | -440.9219 | 9960 | 9519.0781 | 0.28534
|  |  | 48 | 71.7211 | -447.9141 | 9960 | 9512.0859 | 0.28513
|  |  | 49 | 71.436 | -454.9012 | 9960 | 9505.0988 | 0.28493
|  |  | 50 | 71.151 | -461.8831 | 9960 | 9498.1169 | 0.28472
|  |  | 51 | 70.8663 | -468.8599 | 9960 | 9491.1401 | 0.28451
|  |  | 52 | 70.5818 | -475.8316 | 9960 | 9484.1684 | 0.2843
|  |  | 53 | 70.2975 | -482.7981 | 9960 | 9477.2019 | 0.28409
|  |  | 54 | 70.0134 | -489.7595 | 9960 | 9470.2405 | 0.28388
|  |  | 55 | 69.7295 | -496.7159 | 9960 | 9463.2841 | 0.28367
|  |  | 56 | 69.4459 | -503.6671 | 9960 | 9456.3329 | 0.28346
|  |  | 57 | 69.1624 | -510.6132 | 9960 | 9449.3868 | 0.28326
|  |  | 58 | 68.8792 | -517.5542 | 9960 | 9442.4458 | 0.28305
|  |  | 59 | 68.5961 | -524.4901 | 9960 | 9435.5099 | 0.28284
|  |  | 60 | 68.3133 | -531.4209 | 9960 | 9428.5791 | 0.28263
|  |  | 61 | 68.0306 | -538.3466 | 9960 | 9421.6534 | 0.28242
|  |  | 62 | 67.7482 | -545.2672 | 9960 | 9414.7328 | 0.28222
|  |  | 63 | 67.466 | -552.1828 | 9960 | 9407.8172 | 0.28201
|  |  | 64 | 67.184 | -559.0932 | 9960 | 9400.9068 | 0.2818
|  |  | 65 | 66.9022 | -565.9986 | 9960 | 9394.0014 | 0.28159
|  |  | 66 | 66.6206 | -572.8989 | 9960 | 9387.1011 | 0.28139
|  |  | 67 | 66.3392 | -579.7942 | 9960 | 9380.2058 | 0.28118
|  |  | 68 | 66.058 | -586.6844 | 9960 | 9373.3156 | 0.28097
|  |  | 69 | 65.777 | -593.5695 | 9960 | 9366.4305 | 0.28077
|  |  | 70 | 65.4963 | -600.4496 | 9960 | 9359.5504 | 0.28056
|  |  | 71 | 65.2157 | -607.3246 | 9960 | 9352.6754 | 0.28036
|  |  | 72 | 64.9354 | -614.1945 | 9960 | 9345.8055 | 0.28015
|  |  | 73 | 64.6552 | -621.0594 | 9960 | 9338.9406 | 0.27994
|  |  | 74 | 64.3753 | -627.9193 | 9960 | 9332.0807 | 0.27974
|  |  | 75 | 64.0955 | -634.7742 | 9960 | 9325.2258 | 0.27953
|  |  | 76 | 63.816 | -641.6239 | 9960 | 9318.3761 | 0.27933
|  |  | 77 | 63.5367 | -648.4687 | 9960 | 9311.5313 | 0.27912
|  |  | 78 | 63.2575 | -655.3085 | 9960 | 9304.6915 | 0.27892
|  |  | 79 | 62.9786 | -662.1432 | 9960 | 9297.8568 | 0.27871
|  |  | 80 | 62.6999 | -668.9729 | 9960 | 9291.0271 | 0.27851
|  |  | 81 | 62.4214 | -675.7975 | 9960 | 9284.2025 | 0.2783
|  |  | 82 | 62.1431 | -682.6172 | 9960 | 9277.3828 | 0.2781
|  |  | 83 | 61.865 | -689.4319 | 9960 | 9270.5681 | 0.27789
|  |  | 84 | 61.5871 | -696.2415 | 9960 | 9263.7585 | 0.27769
|  |  | 85 | 61.3094 | -703.0462 | 9960 | 9256.9538 | 0.27749
|  |  | 86 | 61.0319 | -709.8458 | 9960 | 9250.1542 | 0.27728
|  |  | 87 | 60.7546 | -716.6405 | 9960 | 9243.3595 | 0.27708
|  |  | 88 | 60.4776 | -723.4301 | 9960 | 9236.5699 | 0.27688
|  |  | 89 | 60.2007 | -730.2148 | 9960 | 9229.7852 | 0.27667
|  |  | 90 | 59.924 | -736.9945 | 9960 | 9223.0055 | 0.27647
|  |  | 91 | 59.6476 | -743.7692 | 9960 | 9216.2308 | 0.27627
|  |  | 92 | 59.3713 | -750.5389 | 9960 | 9209.4611 | 0.27606
|  |  | 93 | 59.0952 | -757.3037 | 9960 | 9202.6963 | 0.27586
|  |  | 94 | 58.8194 | -764.0635 | 9960 | 9195.9365 | 0.27566
|  |  | 95 | 58.5437 | -770.8183 | 9960 | 9189.1817 | 0.27546
|  |  | 96 | 58.2683 | -777.5682 | 9960 | 9182.4318 | 0.27525
|  |  | 97 | 57.993 | -784.3131 | 9960 | 9175.6869 | 0.27505
|  |  | 98 | 57.7179 | -791.0531 | 9960 | 9168.9469 | 0.27485
|  |  | 99 | 57.4431 | -797.7881 | 9960 | 9162.2119 | 0.27465
|  |  | 100 | 57.1685 | -804.5181 | 9960 | 9155.4819 | 0.27444
|  |  | 101 | 56.894 | -811.2432 | 9960 | 9148.7568 | 0.27424
|  |  | 102 | 56.6198 | -817.9634 | 9960 | 9142.0366 | 0.27404
|  |  | 103 | 56.3457 | -824.6787 | 9960 | 9135.3213 | 0.27384
|  |  | 104 | 56.0719 | -831.389 | 9960 | 9128.611 | 0.27364
|  |  | 105 | 55.7982 | -838.0943 | 9960 | 9121.9057 | 0.27344
|  |  | 106 | 55.5248 | -844.7948 | 9960 | 9115.2052 | 0.27324
|  |  | 107 | 55.2516 | -851.4903 | 9960 | 9108.5097 | 0.27304
|  |  | 108 | 54.9785 | -858.1809 | 9960 | 9101.8191 | 0.27284
|  |  | 109 | 54.7057 | -864.8666 | 9960 | 9095.1334 | 0.27264
|  |  | 110 | 54.4331 | -871.5474 | 9960 | 9088.4526 | 0.27244
|  |  | 111 | 54.1606 | -878.2233 | 9960 | 9081.7767 | 0.27224
|  |  | 112 | 53.8884 | -884.8943 | 9960 | 9075.1057 | 0.27204
|  |  | 113 | 53.6164 | -891.5603 | 9960 | 9068.4397 | 0.27184
|  |  | 114 | 53.3445 | -898.2215 | 9960 | 9061.7785 | 0.27164
|  |  | 115 | 53.0729 | -904.8778 | 9960 | 9055.1222 | 0.27144
|  |  | 116 | 52.8014 | -911.5292 | 9960 | 9048.4708 | 0.27124
|  |  | 117 | 52.5302 | -918.1757 | 9960 | 9041.8243 | 0.27104
|  |  | 118 | 52.2592 | -924.8173 | 9960 | 9035.1827 | 0.27084
|  |  | 119 | 51.9883 | -931.4541 | 9960 | 9028.5459 | 0.27064
|  |  | 120 | 51.7177 | -938.086 | 9960 | 9021.914 | 0.27044
|  |  | 121 | 51.4472 | -944.713 | 9960 | 9015.287 | 0.27024
|  |  | 122 | 51.177 | -951.3351 | 9960 | 9008.6649 | 0.27004
|  |  | 123 | 50.907 | -957.9524 | 9960 | 9002.0476 | 0.26985
|  |  | 124 | 50.6371 | -964.5648 | 9960 | 8995.4352 | 0.26965
|  |  | 125 | 50.3675 | -971.1723 | 9960 | 8988.8277 | 0.26945
|  |  | 126 | 50.098 | -977.775 | 9960 | 8982.225 | 0.26925
|  |  | 127 | 49.8288 | -984.3729 | 9960 | 8975.6271 | 0.26905
|  |  | 128 | 49.5597 | -990.9659 | 9960 | 8969.0341 | 0.26886
|  |  | 129 | 49.2909 | -997.554 | 9960 | 8962.446 | 0.26866
|  |  | 130 | 49.0222 | -1004.1374 | 9960 | 8955.8626 | 0.26846
|  |  | 131 | 48.7537 | -1010.7158 | 9960 | 8949.2842 | 0.26826
|  |  | 132 | 48.4855 | -1017.2895 | 9960 | 8942.7105 | 0.26807
|  |  | 133 | 48.2174 | -1023.8583 | 9960 | 8936.1417 | 0.26787
|  |  | 134 | 47.9495 | -1030.4223 | 9960 | 8929.5777 | 0.26767
|  |  | 135 | 47.6819 | -1036.9815 | 9960 | 8923.0185 | 0.26748
|  |  | 136 | 47.4144 | -1043.5358 | 9960 | 8916.4642 | 0.26728
|  |  | 137 | 47.1471 | -1050.0854 | 9960 | 8909.9146 | 0.26708
|  |  | 138 | 46.88 | -1056.6301 | 9960 | 8903.3699 | 0.26689
|  |  | 139 | 46.6131 | -1063.1701 | 9960 | 8896.8299 | 0.26669
|  |  | 140 | 46.3464 | -1069.7052 | 9960 | 8890.2948 | 0.2665
|  |  | 141 | 46.0799 | -1076.2355 | 9960 | 8883.7645 | 0.2663
|  |  | 142 | 45.8136 | -1082.761 | 9960 | 8877.239 | 0.2661
|  |  | 143 | 45.5475 | -1089.2818 | 9960 | 8870.7182 | 0.26591
|  |  | 144 | 45.2816 | -1095.7977 | 9960 | 8864.2023 | 0.26571
|  |  | 145 | 45.0159 | -1102.3088 | 9960 | 8857.6912 | 0.26552
|  |  | 146 | 44.7504 | -1108.8152 | 9960 | 8851.1848 | 0.26532
|  |  | 147 | 44.4851 | -1115.3168 | 9960 | 8844.6832 | 0.26513
|  |  | 148 | 44.22 | -1121.8136 | 9960 | 8838.1864 | 0.26493
|  |  | 149 | 43.955 | -1128.3057 | 9960 | 8831.6943 | 0.26474
|  |  | 150 | 43.6903 | -1134.793 | 9960 | 8825.207 | 0.26454
|  |  | 151 | 43.4257 | -1141.2755 | 9960 | 8818.7245 | 0.26435
|  |  | 152 | 43.1614 | -1147.7532 | 9960 | 8812.2468 | 0.26416
|  |  | 153 | 42.8972 | -1154.2262 | 9960 | 8805.7738 | 0.26396
|  |  | 154 | 42.6333 | -1160.6945 | 9960 | 8799.3055 | 0.26377
|  |  | 155 | 42.3695 | -1167.1579 | 9960 | 8792.8421 | 0.26357
|  |  | 156 | 42.1059 | -1173.6167 | 9960 | 8786.3833 | 0.26338
|  |  | 157 | 41.8425 | -1180.0707 | 9960 | 8779.9293 | 0.26319
|  |  | 158 | 41.5794 | -1186.5199 | 9960 | 8773.4801 | 0.26299
|  |  | 159 | 41.3164 | -1192.9644 | 9960 | 8767.0356 | 0.2628
|  |  | 160 | 41.0536 | -1199.4042 | 9960 | 8760.5958 | 0.26261
|  |  | 161 | 40.791 | -1205.8393 | 9960 | 8754.1607 | 0.26241
|  |  | 162 | 40.5285 | -1212.2696 | 9960 | 8747.7304 | 0.26222
|  |  | 163 | 40.2663 | -1218.6952 | 9960 | 8741.3048 | 0.26203
|  |  | 164 | 40.0043 | -1225.1161 | 9960 | 8734.8839 | 0.26184
|  |  | 165 | 39.7424 | -1231.5322 | 9960 | 8728.4678 | 0.26164
|  |  | 166 | 39.4808 | -1237.9437 | 9960 | 8722.0563 | 0.26145
Note on B6: Bob Glicksman: http://www.rapidtables.com/convert/power/ton-to-kw.htm
Note on A16: Bob Glicksman: http://en.wikipedia.org/wiki/Coefficient_of_performance
Note on B29: Bob Glicksman: http://www.rapidtables.com/convert/energy/BTU_to_kWh.htm; 76000 BTU per gallon EtOH
Note on B30: Bob Glicksman: Thermostat will cut off refrigeration at desired temp of 40 deg F and hold it there